## manually
|  | Pump Tank Gallons Per Inch and drawdown test | [9 empty] | www.SepticResource.com (vers 19.2)
| Property Owner: | [8 empty] | Date:
| Site Address: | [8 empty] | PID:
Comments:
There are a few options for determining a pump tanks "Gallons Per Inch" value, we will start with the easiest.
You only need to figure out 1 way, and can leave the rest blank.
GPI
1) | If you happen to know the tank model and GPI, simply enter it here: | [10 empty] | gallons per inch
2) | Or, If you know the volume of the tank in gallons, then measure the distance from the inside bottom of the tank
to the outlet invert (bottom of the outlet pipe)(in inches). Enter both values here:
|  | 0 | gallon tank |  |  |  | 0.001 | inches from inside bottom to outlet invert
[9 empty] | now divide tank gallons by the depth in inches= | 0 | gallons per inch
3) | Or, If you can measure the inside length and width (or diameter) of the tank, we can calculate the gpi.
if rectangular tank - take the inside length and width in inches and mulitply together, then divide by 231
| length |  | times | width |  | divide by 231 |  | 0 | gallons per inch
| if Round Tank enter inside diameter here: | [7 empty] | (the diameter is from one side to the other)
[5 empty] | divide the diameter by 2 = |  |  |  | 0 | (this is the radius)
now take the radius * itself, * 3.14 then divide by 231
|  |  | 0 | radius times |  | 0 | radius times |  | 3.14 | divided by |  | 231 | = | 0 | gal per inch
OR
| If you can measure the outside length and width (or diameter) of the tank, we can calculate the gpi. | [15 empty] | 0
| if rectangular tank - take the outside length and width in inches, then subtract 6" from each measurement | [15 empty] | 0
| for tank wall thickness, then multiply together, then divide by 231. | [15 empty] | 0
|  |  | (length - 6" = ) |  | times (width - 6" = ) |  |  |  | divide by 231 |  | 0 | gallons per inch |  |  |  |  | 0
0
| if Round Tank enter outside diameter - 6" here: | [7 empty] | (the diameter is from one side to the other)
[5 empty] | divide the diameter by 2 = |  |  |  | 0 | (this is the radius)
now take the radius * itself, * 3.14 then divide by 231
|  |  | 0 | radius times |  | 0 | radius times |  | 3.14 | divided by |  | 231 | = | 0 | gal per inch
PUMP DRAWDOWN test:
Here we will determine the flow rate of the pump in Gallons per Minute - GPM.
| Measure the water level in the tank from some fixed point (top of riser) - in inches | [13 empty] | 0 | inches
Run the pump for 2-4 minutes (make sure you have enough water) and record the time
|  | (record in fractions of a minute: 15 sec =.25, 30 sec =.5, 45 sec =.75 etc.) | [10 empty] | 0 | minutes
| As soon as the pump turns off measure water height again from the same point (before drainback) | [13 empty] | 0 | inches
If the drainfeild is more than 50' or so away, measure the water height again after drainback has stopped
[15 empty] | 0 | inches
[11 empty] | leads to pump out of |  |  |  | 0 | inches
|  | 0 | inches pumped out at |  |  | 0 | gpi = | 0 | gallons pumped, in |  |  | 0 | minutes = |  | #DIV/0! | GPM
|  | with | 0 | gallons of drainback
| Enter the design flow | [6 empty] | 0 | gallons
| Enter the number of doses per day (peak flow) | [6 empty] | 0 | doses |  |  | plus drainback of |  |  | 0 | gal
Leads to:
|  | AVERAGE time dosing of | [5 empty] | #DIV/0! | minutes ON and |  |  | #DIV/0! | minutes OFF
|  | and PEAK time dosing of | [5 empty] | #DIV/0! | minutes ON and |  |  | #DIV/0! | minutes OFF
|  | with a tank at | [5 empty] | 0 | GPI
|  | and a pump rate of | [5 empty] | #DIV/0! | GPM
Calculations are deemed reliable for estimation purposes only.
| Designer Signature |  |  |  |  | Company |  |  |  |  | License# |  |  | Date

## online
|  | Pump Tank GPI determination & drawdown test | [9 empty] | www.SepticResource.com (vers 18.2)
| Property Owner: | [8 empty] | Date:
| Site Address: | [8 empty] | PID:
Comments:
| instructions: |  |  | = req'd input | [5 empty] | = self-calculated (DO NOT ADJUST)
There are a few options for determining a pump tanks "Gallons Per Inch" value, we will start with the easiest.
You only need to figure out 1 way, and can leave the rest blank.
1) | If you know the tank model and GPI, simply enter it here:
|  |  | 0 | gallons per inch
2) | Or, If you know the volume of the tank in gallons, then measure the distance from the inside bottom of the tank
to the bottom of the outlet pipe (in inches). Enter both values here:
|  |  | 0 | gallons
|  |  | 0 | inches
|  |  | 0 | gallons per inch
3) | Or, If you can measure the inside length and width (or diameter) of the tank, OR
| the outside length and width (or diameter) of the tank, | [7 empty] | from those measurements we can calculate the GPI.
| Enter the inside dimensions of the tank. | [6 empty] | if Round Tank enter inside dimentions here:
|  | Length | 0 | inches |  |  |  | (the diameter is from one side all the way to the other)
|  | Width | 0 | inches |  |  |  |  | Diameter | 0 | inches
|  |  | 0 | gpi | [5 empty] | 0 | gpi | [5 empty] | 0
OR
| Enter the outside dimensions of the tank. | [6 empty] | if Round Tank enter outside dimensions here:
(the spread sheet will assume 3" thick walls and factor that out of the results)
|  | Length | 0 | inches |  |  |  | (the diameter is from one side all the way to the other)
|  | Width | 0 | inches |  |  |  |  | Diameter | 0 | inches | [5 empty] | 0.15584 | 0.12234
|  |  | 0 | gpi | [5 empty] | 0 | gpi | [5 empty] | 0
0
| PUMP DRAWDOWN test: | [15 empty] | 0
| Here we will determine the flow of the pump in Gallons per Minute - GPM. | [15 empty] | 0
| Measure the water level in the tank from some fixed point (top of riser) - in inches | [13 empty] | 0 | inches
Run the pump for 2-4 minutes (make sure you have enough water) and record the time
|  | (record in fractions of a minute: 15 sec = .25, 20 sec = .33, 30 sec = .5, etc.) | [10 empty] | 0 | minutes
| As soon as the pump turns off measure water height again from the same point (before drainback) | [13 empty] | 0 | inches
If the drainfeild is more than 50' or so away, measure the water height again after drainback has stopped
[15 empty] | 0 | inches
[11 empty] | leads to pump out of |  |  |  | 0 | inches
|  |  | 0 | inch pump out |  | 0 | gpi = | 0 | gallons pumped in |  |  | 0 | minutes = |  | #DIV/0! | GPM
|  | with | 0 | gallons of drainback
| enter the design flow | [7 empty] | 0 | gallons
| enter the number of doses per day (peak flow) | [7 empty] | 0 | doses |  | plus drainback of |  |  | 0
| leads to AVERAGE time dosing of | [7 empty] | #DIV/0! | minutes ON and |  |  | #DIV/0! | minutes OFF
| and PEAK time dosing of | [7 empty] | #DIV/0! | minutes ON and |  |  | #DIV/0! | minutes OFF
| with a tank at |  |  | 0 | GPI
| and a pump rate of |  |  | #DIV/0! | GPM
Calculations are deemed reliable for estimation purposes only.
| Designer Signature |  |  |  |  | Company |  |  |  |  | License# |  |  | Date